# Zero-Config MAC Address for MS/TP

Problem:

There is a need to create low cost MS/TP devices that do not include hardware (LCD and buttons, DIP switch, numeric dials, jumpers, etc) for configuring their MAC address.  The MS/TP Master Node device needs a MAC address in order to participate in token passing.  However, a device cannot be assigned a MAC address without receiving a message, and it cannot receive the message because any potential sender would not know the device's MAC address.

Proposed Solution:

This proposal describes a scheme for allowing devices to choose their own MAC address after monitoring the MS/TP line for available MAC addresses indicated by unanswered PollForMaster frames.

Since the token passes rapidly between nodes, and we must assume that the zero-configuration process may occur in the presence of statically configured nodes executing the current 135-2010 or earlier state machine, the only real opportunity to inject packet without holding a Token comes during the Poll For Master sequence.

- Assume the node has listened to the token passing for a while and selected an address at random (or a previously  used address) from the list of addresses that appear to be available.  The addresses will be selected from a range of 64 to 127, leaving addresses 0 to 64 for fixed address nodes which will reduce the likelihood of collisions due to variable start up time.

- Simply sending a Reply To Poll For Master is not enough of a confirmation, because there would be no way to distinguish nodes through their UIDs, nor to distinguish a dynamically addressed node from a statically configured node that happened to come online at that time.

- After responding with a Reply To Poll For Master frame at an unused address, and receiving a Token frame, a Test Request frame will be sent by a node wishing to claim an address. The Test Request frame will include some unique information in the Data portion of the frame.  This will cause the Poll For Master and Token sending node to reply with a Test Response frame which will include the unique data.

- The zero configuration node will already have a list of peers, and can simply pass the Token to the Next Station, and continue with the normal Master Node State Machine.

- The zero configuration node will monitor all MS/TP traffic, and will stop using its chosen MAC address if it sees another node communicating with an identical source MAC.  The zero configuration node will start searching for another MAC at that time.  The monitoring can be easily done after some modification to the DataNotForUs transition and SKIP_DATA state of the Receive Node Finite State Machine for nodes that support Automatic Addressing of MS/TP.

This scheme was proposed during BACnet MS/TP working group meetings in Salt Lake City in June, 2008.  The zero-configuration scheme was researched and developed, and actually implemented into products in May of 2010 to verify the approach, prior to creating this proposal in October of 2010.

History

STK-030-1:

Discussed at MS/TP working group meeting in Atlanta in October, 2010.  Discussed even/odd address ranges, and changing the range from 32..127 to 64..127.

STK-030-2:

Changed the zero configuration node address range from 32..127 to 64..127 after meeting discussion that indicated a need for a larger number of fixed address slots.

STK-030-3:

Changed the concept to use the "preferred" or remembered address when it is available.

STK-030-4:

Changed the language of "preferred" address to indicate mandatory usage.  Changed the format of the unique data appended to the Test Request message to be explicitly defined and aligned with the BACnet Serial Number (Addendum 2008ak).

STK-030-5:

Change the language to make the new states clearly optional.

STK-030-6:

removed the word 'random' from the maintained address in 9.4.1

STK-030-7:

added Enable  property in the network port object

STK-030-8:

remove color highlighting

STK-030-9:

Change the references to refer to 135-2012.  Changed ZeroConfigurationMaster to ZeroConfigurationMode, and Zero_Configuration_Master_Enable to Zero_Configuration_Mode_Enable.  Changed phrases "this node supports Automatic Addressing of MS/TP" to "and ZeroConfigurationMode is TRUE".  Fixed Parameter and Variable subscripts.  Fixed indentation. Changed wording referencing Network Port object.

STK-030-10:

Made allowance for Serial_Number property being optional.

STK-030-11:

Removed Serial Number, Vendor ID, and Model Number dependency and replaced with UUID.

STK-030-12:

Added State Diagrams

STK-030-13:

Converted  ZeroConfigurationMode to reference TRUE or FALSE, and devices not implementing zero-configuration mode will always be FALSE.  Updated language for Network Port object according to latest addendum.

STK-030-14:

Fixed text in State Diagram.

STK-030-15

Fixed Annex A changes.

Changes to ASHRAE Standard 135: (reference: 135-2012)

[Insert new 9.4.1 Automatic Addressing of MS/TP Nodes, p. 94]

9.4.1	Automatic Addressing of MS/TP Nodes

While many MS/TP nodes will be configured with a static address through DIP switches, rotary dials, or proprietary software configuration, certain implementations may be dynamically configured through an automatic addressing mechanism.

A "zero-configuration auto-addressing mode" node is an MS/TP master node that does not begin with a preconfigured MS/TP address, and chooses an MS/TP address after monitoring the frames for an unused address.  The node will use the Test Request and Test Response frames for address confirmation, by including some information in the Data portion of the frame that is unique to the node.  Additionally, the node will constantly monitor all MS/TP frames, and will choose another MAC address if it sees another node using its chosen MAC address.  Once the node chooses and confirms an MS/TP MAC address, it shall use this address in the token passing.  It is required to maintain this address across device restarts and loss of power and use the address as its preferred address when it restarts.  The node shall use a range of MS/TP addresses from 64 to 127 (64 addresses), which allows fixed addresses to exist from 0 to 63 (64 addresses).  The node shall use a Max_Master that is fixed at 127.

[add to 9.5.2, Variables pp. 95-96]

9.5.2	Variables

...

ZeroConfigurationMode	A Boolean flag set to TRUE if this node is a zero configuration master node.

Address List	A list, used by a ZeroConfigurationMode node, that tracks the used and available MS/TP addresses, along with which devices have passed a Token or Poll For Master frame (master nodes).

ReceivedValidFrameNotForUs	Boolean flag set to TRUE by the Receive State Machine if a valid frame is received that is not addressed to TS. Set to FALSE by the Master node state machine.

ZeroConfigurationAddress	A Master node address, chosen randomly from the Address List.  A successful chosen address shall be stored in non-volatile memory across device restarts and loss of power, and shall be used during the first attempt to confirm the address.  Subsequent address confirmation attempts, if needed, must use a randomly chosen address to prevent deadlock. Success is indicated by responding to a BACnet Data Expecting Reply or a BACnet Data Not Expecting Reply frame for nodes that have a BACnet Application layer.

ZeroConfigurationUUID	A 16 octet UUID (Universally Unique IDentifier) that conforms to RFC-4122.

[add to 9.5.3 Parameters, pp. 96-97]

9.5.3	Parameters

...

Tconfirmation_timeout	The minimum time without a DataAvailable or ReceiveError event that a node must wait for a station to begin replying to a Test Request: 300 milliseconds.

...

[Change Figure 9-3. Receive Frame State Machine, p. 97]

[add transition line NotForUsZeroConfigurationMode from HEADER_CRC to IDLE]

[add transition line DataNotForUsZeroConfigurationMode from HEADER_CRC to SKIP_DATA]

[add transition line DataOctetZeroConfigurationMode from  SKIP_DATA to SKIP_DATA]

[add transition line SkipDataOctet from SKIP_DATA to SKIP_DATA]

[add transition line CRC1 from SKIP_DATA to SKIP_DATA]

[add transition line CRC2 from SKIP_DATA to SKIP_DATA_CRC]

[add state SKIP_DATA_CRC]

[add transition line BadCRC from SKIP_DATA_CRC to IDLE]

[add transition line GoodCRC from SKIP_DATA_CRC to IDLE]

[Change 9.5.4.4, HEADER_CRC, p. 99]

9.5.4.4	HEADER_CRC

In the HEADER_CRC state, the node validates the CRC on the fixed message header.

BadCRC

If the value of HeaderCRC is not X '55',

then set ReceivedInvalidFrame to TRUE to indicate that an error has occurred during the reception of a frame, and enter the IDLE state to wait for the start of the next frame.

NotForUs

If the value of the HeaderCRC is X '55' and DataLength is zero and the value of DestinationAddress is not equal to either TS (this station) or 255 (broadcast) and ZeroConfigurationMode is FALSE,

then enter the IDLE state to wait for the start of the next frame.

NotForUsZeroConfigurationMode

If the value of the HeaderCRC is X '55' and DataLength is zero and the value of DestinationAddress is not equal to either TS (this station) or 255 (broadcast) and ZeroConfigurationMode is TRUE,

then set ReceivedValidFrameNotForUs to TRUE to indicate that a frame with no data has been received and is not for us, and enter the IDLE state to wait for the start of the next frame.

DataNotForUs

If the value of the HeaderCRC is X '55' and DataLength is not zero and the value of DestinationAddress is not equal to either TS (this station) or 255 (broadcast) and ZeroConfigurationMode is TRUE,

then set Index to zero and enter the SKIP_DATA state to consume the data and data CRC portions of the frame.

DataNotForUsZeroConfigurationMode

If the value of the HeaderCRC is X '55' and DataLength is not zero and the value of DestinationAddress is not equal to either TS (this station) or 255 (broadcast) and ZeroConfigurationMode is TRUE,

then set Index to zero; set DataCRC to X'FFFF'; and enter the SKIP_DATA state to receive the data and data CRC portions of the frame.

...

[change 9.5.4.7, SKIP_DATA, p. 101]

9.5.4.7	SKIP_DATA

In the SKIP_DATA state, the node waits for the data portion of a frame to be received so that its contents can be ignored. either ignored, or consumed if ZeroConfigurationMode is TRUE.

...

DataOctet

If ReceiveError is FALSE and DataAvailable is TRUE and Index is less than DataLength+1 and ZeroConfigurationMode is TRUE,

then set DataAvailable to FALSE; set SilenceTimer to zero; increment Index by 1; and enter the SKIP_DATA state.

Done

If ReceiveError is FALSE and DataAvailable is TRUE and Index is equal to DataLength+1 and ZeroConfigurationMode is FALSE,

then set DataAvailable to FALSE; set SilenceTimer to zero; and enter the IDLE state to wait for the start of the next frame.

DataOctetZeroConfigurationMode

If ReceiveError is FALSE and DataAvailable is TRUE and Index is less than DataLength+1 and Index is less than InputBufferSize and ZeroConfigurationMode is TRUE,

then set DataAvailable to FALSE; set SilenceTimer to zero; accumulate the contents of DataRegister into DataCRC; save the contents of DataRegister at InputBuffer[Index]; increment Index by 1; and enter the SKIP_DATA state.

SkipDataOctet

If ReceiveError is FALSE and DataAvailable is TRUE and Index is less than DataLength+1 and Index is greater than or equal to InputBufferSize and ZeroConfigurationMode is TRUE,

then set DataAvailable to FALSE; set SilenceTimer to zero; accumulate the contents of DataRegister into DataCRC; increment Index by 1; and enter the SKIP_DATA state.

CRC1

If ReceiveError is FALSE and DataAvailable is TRUE and Index is equal to DataLength and ZeroConfigurationMode is TRUE,

then set DataAvailable to FALSE; set SilenceTimer to zero; accumulate the contents of DataRegister into DataCRC; increment Index by 1; and enter the SKIP_DATA state.

CRC2

If ReceiveError is FALSE and DataAvailable is TRUE and Index is equal to DataLength plus 1 and ZeroConfigurationMode is TRUE,

then set DataAvailable to FALSE; set SilenceTimer to zero; accumulate the contents of DataRegister into DataCRC; and enter the SKIP_DATA_CRC state.

[add to 9.5.4, Receive Frame Finite State Machine, pp. 97-101]

9.5.4.X	SKIP_DATA_CRC

In the SKIP_DATA_CRC state, the node validates the CRC of the message data not for us if ZeroConfigurationMode is TRUE.

BadCRC

If the value of DataCRC is not X'F0B8',

then set ReceivedInvalidFrame to TRUE to indicate that an error has occurred during the reception of a frame, and enter the IDLE state to wait for the start of the next frame.

GoodCRC

If the value of DataCRC is X'F0B8',

then set ReceivedValidFrameNotForUs to TRUE to indicate the complete reception of a valid frame that is not for us, and enter the IDLE state to wait for the start of the next frame.

[change Figure 9-4. Master Node State Machine., p. 103]

[add transition InitializeZeroConfigurationMaster from INITIALIZE to ZERO_CONFIGURATION_IDLE]

[add state ZERO_CONFIGURATION_IDLE and transitions]

[add state ZERO_CONFIGURATION_PFM and transitions]

[add state ZERO_CONFIGURATION_TOKEN and transitions]

[add state ZERO_CONFIGURATION_CONFIRM and transitions]

[change 9.5.6.1 INITIALIZE, pp. 103-104]

9.5.6.1	INITIALIZE

When a master node is powered up or reset, it shall unconditionally enter the INITIALIZE state.

InitializeZeroConfigurationMaster

If ZeroConfigurationMode is TRUE,

then set TS to 255, and enter the ZERO_CONFIGURATION_IDLE state.

DoneInitializing

Unconditionally,  If ZeroConfigurationMode is FALSE,

then set TS to the node's station address, set NS equal to TS (indicating that the next station is unknown), set PS equal to TS, set TokenCount to Npoll (thus causing a Poll For Master to be sent when this node first receives the token), set SoleMaster to FALSE, set ReceivedValidFrame and ReceivedInvalidFrame to FALSE, and enter the IDLE state.

[add to 9.5.6, Master Node Finite State Machine, pp. 102-109]

9.5.6.X1	ZERO_CONFIGURATION_IDLE

The ZERO_CONFIGURATION_IDLE state is entered when the node's station address is unknown (TS=255), and ZeroConfigurationMode is TRUE.

ReceivedBroadcast

If ReceivedValidFrame is TRUE, and the SourceAddress does not exist in our Address List,

then the SourceAddress is in use.  Store the SourceAddress from the frame in an Address List to indicate that the address is in use. Set ReceivedValidFrame to FALSE, and enter the ZERO_CONFIGURATION_IDLE state to wait for the next frame.

ReceivedFrame

If ReceivedValidFrameNotForUs is TRUE, and the FrameType is not Poll For Master,

then the SourceAddress is in use.  Store the SourceAddress from the frame in an Address List to document that the address is in use, and note in the Address List if the frame was a Token frame (so this node can find its peer). Set ReceivedValidFrameNotForUs to FALSE, and enter the ZERO_CONFIGURATION_IDLE state to wait for the next frame.

InvalidFrame

If ReceivedInvalidFrame is TRUE,

then an invalid frame was received. Set ReceivedInvalidFrame to FALSE, and enter the ZERO_CONFIGURATION_IDLE state to wait for the next frame.

StorePotentialAddress

If ReceivedValidFrameNotForUs is TRUE, FrameType is equal to Poll For Master, and the DestinationAddress is not marked in the Address List as Poll For Master address,

then this address is potentially unused.  Store the DestinationAddress from the frame in the Address List to document that the address is a Poll For Master frame. Set ReceivedValidFrameNotForUs to FALSE, and enter the ZERO_CONFIGURATION_IDLE state to wait for the next frame.

ValidAddressAvailable

If ReceivedValidFrameNotForUs is TRUE, FrameType is equal to Poll For Master, and the DestinationAddress is marked in the Address List as a Poll For Master Address,

then the Poll For Master cycle has completed for all the devices.  Set TS to the ZeroConfigurationAddress, chosen from all of the unused addresses in the Address List marked as Poll For Master addresses.  Set ReceivedValidFrame to FALSE, set  ReceivedValidFrameNotForUs to FALSE, and enter the ZERO_CONFIGURATION_PFM state to wait for the next frame.

NoAddressAvailable

If ReceivedValidFrame is TRUE or ReceivedValidFrameNotForUs is TRUE, and the SourceAddress exists in the Address List, and there are no unused addresses in the Address List that are between 64 and 127, inclusive,

then the address monitor cycle is complete.  Set ReceivedValidFrame to FALSE, set  ReceivedValidFrameNotForUs to FALSE, and enter the ZERO_CONFIGURATION_IDLE state to wait for the next frame.

LostToken

If SilenceTimer is greater than or equal to Tno_token + (127 * Tslot) + (TS* Tslot) (where TS is the ZeroConfigurationAddress),

then assume that the token has been lost. Set TS to the ZeroConfigurationAddress, chosen from the set of unused addresses in the Address List between 64 and 127, inclusive.  Call SendFrame to transmit a Test Request frame to TS with a ZeroConfigurationUUID in the Data portion of the frame; enter the ZERO_CONFIGURATION_CONFIRM state to wait for a Test Response.

9.5.6.X2	ZERO_CONFIGURATION_PFM

The ZERO_CONFIGURATION_PFM state is entered when a node is waiting for a Poll For Master frame sent to the ZeroConfigurationAddress it has chosen, and ZeroConfigurationMode is TRUE

TestRequestFromUs

If ReceivedValidFrame is TRUE or ReceivedValidFrameNotForUs is TRUE, and the FrameType is Test Request, and the SourceAddress is equal to TS or the DestinationAddress is equal to TS,

then another node chose our address.  Clear all the flags and addresses from the Address List, set ReceivedValidFrame to FALSE, set ReceivedValidFrameNotForUs to FALSE, set TS to 255, and enter the ZERO_CONFIGURATION_IDLE state to wait for the next frame.

PollForMasterFromUs

If ReceivedValidFrame is TRUE or ReceivedValidFrameNotForUs is TRUE, and the FrameType is Poll For Master, and the SourceAddress is equal to TS,

then another node is using our address.  Clear all the flags and addresses from the Address List, set ReceivedValidFrame to FALSE, set ReceivedValidFrameNotForUs to FALSE, set TS to 255, and enter the ZERO_CONFIGURATION_IDLE state to wait for the next frame.

PollForMasterForUs

If ReceivedValidFrame is TRUE, and the FrameType is Poll For Master, and the DestinationAddress is equal to TS,

then respond.  Call SendFrame to transmit a Reply To Poll For Master frame to the node whose address is specified by SourceAddress (Source Address of the Poll); set ReceivedValidFrame to FALSE; and enter the ZERO_CONFIGURATION_TOKEN state to wait for a Token frame.

FrameFromUs

If ReceivedValidFrame is TRUE or ReceivedValidFrameNotForUs is TRUE, and the FrameType is not Test Request, and the Frame Type is not Poll For Master, and the SourceAddress is equal to TS,

then another node chose our address.  Clear all the flags and addresses from the Address List, set ReceivedValidFrame to FALSE, set ReceivedValidFrameNotForUs to FALSE, set TS to 255, and enter the ZERO_CONFIGURATION_IDLE state to wait for the next frame.

InvalidFrame

If ReceivedInvalidFrame is TRUE,

then wait for another frame.  Enter the ZERO_CONFIGURATION_PFM state to wait for the a Poll For Master frame addressed to us.

LostToken

If SilenceTimer is greater than or equal to Tno_token + (127 * Tslot) + (TS* Tslot) (where TS is the ZeroConfigurationAddress),

then assume that the token has been lost. Clear all the flags and addresses from the Address List, set ReceivedValidFrame to FALSE, set ReceivedValidFrameNotForUs to FALSE, set TS to 255, and enter the ZERO_CONFIGURATION_IDLE state to wait for the next frame.

9.5.6.X3	ZERO_CONFIGURATION_TOKEN

The ZERO_CONFIGURATION_TOKEN state is entered when a node is waiting for a Token frame from the master to which it previously sent a Reply To Poll For Master frame, and ZeroConfigurationMode is TRUE

TokenForUs

If ReceivedValidFrame is TRUE, and the FrameType is Token, and the DestinationAddress is equal to TS,

then confirm that we can use this address.  Set ReceivedValidFrame to FALSE; Call SendFrame to transmit a Test Request frame to the node whose address is specified by SourceAddress (Source Address of the Token), and include the ZeroConfigurationUUID in the Data portion of the frame;  Enter the ZERO_CONFIGURATION_CONFIRM state to wait for a Test Response.

FrameNotTokenForUs

If ReceivedValidFrame is TRUE or ReceivedValidFrameNotForUs is TRUE, and the FrameType is not Token,

then restart the process.  Clear all the flags and addresses from the Address List, set ReceivedValidFrame to FALSE, set ReceivedValidFrameNotForUs to FALSE, set TS to 255, and enter the ZERO_CONFIGURATION_IDLE state to wait for the next frame.

InvalidFrame

If ReceivedInvalidFrame is TRUE,

then wait for another frame.  Enter the ZERO_CONFIGURATION_TOKEN state to wait for the Token frame addressed to us.

LostToken

If SilenceTimer is greater than or equal to Tno_token + (127 * Tslot) + TS* Tslot) (where TS is the ZeroConfigurationAddress),

then assume that the token has been lost. Clear all the flags and addresses from the Address List, set ReceivedValidFrame to FALSE, set ReceivedValidFrameNotForUs to FALSE, set TS to 255, and enter the ZERO_CONFIGURATION_IDLE state to wait for the next frame.

9.5.6.X4	ZERO_CONFIGURATION_CONFIRM

The ZERO_CONFIGURATION_CONFIRM state is entered when a node is waiting for a Test Reponse frame. and ZeroConfigurationMode is TRUE.

ConfirmationTimeout

If SilenceTimer is greater than or equal to Tconfirmation_timeout,

then use the Address.  Set PS to TS; set NS to TS (no known successor node); set RetryCount and EventCount to zero; set TokenCount to Npoll (thus causing a Poll For Master to be sent when this node first receives the token), and set SoleMaster to FALSE; and enter the POLL_FOR_MASTER state to find a new successor to TS.

InvalidFrame

If SilenceTimer is less than Tconfirmation_timeout and ReceivedInvalidFrame is TRUE,

then an invalid frame was received. Set ReceivedInvalidFrame to FALSE, Clear all the flags and addresses from the Address List, set TS to 255, and enter the ZERO_CONFIGURATION_IDLE state to wait for the next frame.

ConfirmationSuccessful

If SilenceTimer is less than Tconfirmation_timeout, ReceivedValidFrame is TRUE, FrameType is Test Response, and the Data sent in the Test Request match,

then use the Address.  Set PS to TS; call SendFrame to transmit a Token frame to NS (found by looking at Address List entries with Token marked); set RetryCount and EventCount to zero; set TokenCount to one; and enter the PASS_TOKEN state.

ConfirmationFailed

If SilenceTimer is less than Tconfirmation_timeout, ReceivedValidFrame is TRUE, and FrameType is Test Response and Data sent in the Test Request does not match, or the FrameType is not Test Response,

then start over.  Set ReceivedFrame to FALSE; Clear all the flags and addresses from the Address List; Set TS to 255;  Enter the ZERO_CONFIGURATION_IDLE state to wait for the next frame.

[add the following state transitions to 9.5.6.2, IDLE, pp. 104-105, 9.5.6.4 WAIT_FOR_REPLY, pp. 105-106, and 9.5.6.8 POLL_FOR_MASTER, pp. 107-109]

9.5.6.2	IDLE

9.5.6.4	WAIT_FOR_REPLY

9.5.6.8	POLL_FOR_MASTER

...

ReceivedValidFrameFromUs

If ReceivedValidFrameNotForUs is TRUE, and SourceAddress is equal to TS, and ZeroConfigurationMode is TRUE,

then another node is using our ZeroConfigurationAddress.  Set ReceivedValidFrameNotForUs to FALSE; Clear all the flags and addresses from the Address List; Set TS to 255; Enter the ZERO_CONFIGURATION_IDLE state to wait for the next frame.

ReceivedValidFrameNotForUs

If ReceivedValidFrameNotForUs is TRUE, and SourceAddress is not equal to TS, and ZeroConfigurationMode is TRUE,

then discard the frame.  Set ReceivedValidFrameNotForUs to FALSE; Enter the IDLE state to wait for the next frame.

...

[add to 12.X, Network Port object]

12.X	Network Port Object

…

Table 12-X. Properties of the Network Port Object Type

| Property Identifier | Property Datatype | Conformance Code |
| --- | --- | --- |
| … |  |  |  |
| Zero_Configuration_Mode_Enable | BOOLEAN | ON |  |
| … |  |  |  |

…

N Required if the port is an MS/TP port and the device supports MS/TP ZeroConfigurationMode.

…

12.X.Y	Zero_Configuration_Mode_Enable

This property, of type BOOLEAN, indicates whether or not MS/TP ZeroConfigurationMode is enabled. A value of TRUE indicates that ZeroConfigurationMode is enabled, FALSE indicates it is not.

This property is required if MS/TP ZeroConfigurationMode is supported by this network port.

If this property is writable, then a successful write to this property shall set the Changes_Pending property to TRUE. A value written to this property shall become effective when the  device receives a ReinitializeDevice service request with a 'Reinitialized State of Device' of ACTIVATE_CHANGES  or WARMSTART.

[add to ANNEX A), pg 776]

...

Data Link Layer Options:

…

( MS/TP master (Clause 9), baud rate(s):

( MS/TP zero configuration master (Clause 9), baud rate(s):

…